## Slide 1: Perencanaan Sistem Listrik untuk Industri TEL 12072
Oleh
Dr Ir Dina Maizana MT
maizanadina@gmail.com
Universitas Medan Area
Fakultas Teknik

## Slide 2: Mari kita berdoa menurut agama dan kepercayaan masing-masing sebelum kelas dimulai.
Doa dimulai…

## Slide 3: Agenda
Kebutuhan daya (Power Demand)
Aliran daya (Power Flow)
Arus beban ( Load Current)
Proteksi gangguan (Protection on Fault)
Cadangan daya ( Power Standby)
Unbreakable PS
Harmonik (Harmonics)
Pentanahan (Grounding)
Penangkal petir (Lightning rod)
Kapasitor bank ( Bank Capacitor)
Keselamatan (Savings)

## Slide 4: Cadangan daya ( Power Standby)
A standby generator is a back-up electrical system that operates automatically.[1]
  Within seconds of a utility outage an automatic transfer switch senses the power loss, commands the generator to start and then transfers the electrical load to the generator. The standby generator begins supplying power to the circuits.[2]
After utility power returns, the automatic transfer switch transfers the electrical load back to the utility and signals the standby generator to shut off.
  It then returns to standby mode where it awaits the next outage.
  To ensure a proper response to an outage, a standby generator runs weekly self-tests.
  Most units run on diesel, natural gas, or liquid propane gas.[3]

## Slide 5
The packaged combination of a diesel engine, a generator and various ancillary devices (such as base, canopy, sound attenuation, control systems, circuit breakers, jacket water heaters and starting system) is referred to as a "generating set" or a "genset" for short.

## Slide 6
Set sizes range :
  8 to 30 kW (also 8 to 30 kVA single phase) for homes, small shops and offices
  8 kW (11 kVA) for the larger industrial generators
  up to 2,000 kW (2,500 kVA three phase) used for large office complexes, factories.
  200 kW (250 kVA) are widely used not only for emergency power, but also many have a secondary function of feeding power to utility grids either during peak periods, or periods when there is a shortage of large power generators.

## Slide 7
Generator size
Generating sets are selected based on the electrical load
  they are intended to supply,
  the electrical load's characteristics such as kW, kVA, var, harmonic content, surge currents (e.g., motor starting current) and non-linear loads.
  The expected duty (such as emergency, prime or continuous power) as well as environmental conditions (such as altitude, temperature and exhaust emissions regulations) must also be considered.

## Slide 8
One or more diesel generators operating without a connection to an electrical grid are referred to as operating in island mode.
Operating generators in parallel provides the advantage of redundancy, and can provide better efficiency at partial loads.
The plant brings generator sets online and takes them off line depending on the demands of the system at a given time.
An islanded power plant intended for primary power source of an isolated community will often have at least three diesel generators, any two of which are rated to carry the required load.

## Slide 9
Generators can be electrically connected together through the process of synchronization.
Synchronization involves matching voltage, frequency and phase before connecting the generator to the system.
Failure to synchronize before connection could cause a high short circuit current or wear and tear on the generator or its switchgear.
The synchronization process can be done automatically by an auto-synchronizer module, or manually by the instructed operator.
The auto-synchronizer will read the voltage, frequency and phase parameters from the generator and busbar voltages, while regulating the speed through the engine governor or ECM (Engine Control Module).

## Slide 10
Load can be shared among parallel running generators through load sharing.
Load sharing can be achieved by using drop speed control controlled by the frequency at the generator, while it constantly adjusts the engine fuel control to shift load to and from the remaining power sources.
A diesel generator will take more load when the fuel supply to its combustion system is increased, while load is released if fuel supply is decreased.

## Slide 11
Generator Rating Definitions
Standby Rating based on Applicable for supplying emergency power for the duration of normal power interruption. No sustained overload capability is available for this rating. (Equivalent to Fuel Stop Power in accordance with ISO3046, AS2789, DIN6271 and BS5514). Nominally rated.
Typical application - emergency power plant in hospitals, offices, factories etc. Not connected to grid.
Prime (Unlimited Running Time) Rating: Should not be used for Construction Power applications. Output available with varying load for an unlimited time. Typical peak demand 100% of prime-rated ekW with 10% of overload capability for emergency use for a maximum of 1 hour in 12. A 10% overload capability is available for limited time. (Equivalent to Prime Power in accordance with ISO8528 and Overload Power in accordance with ISO3046, AS2789, DIN6271, and BS5514). This rating is not applicable to all generator set models.
Typical application - where the generator is the sole source of power for say a remote mining or construction site, fairground, festival etc.

## Slide 12
Base Load (Continuous) Rating based on: Applicable for supplying power continuously to a constant load up to the full output rating for unlimited hours. No sustained overload capability is available for this rating. Consult authorized distributor for rating. (Equivalent to Continuous Power in accordance with ISO8528, ISO3046, AS2789, DIN6271, and BS5514). This rating is not applicable to all generator set models
Typical application - a generator running a continuous unvarying load, or paralleled with the mains and continuously feeding power at the maximum permissible level 8,760 hours per year. This also applies to sets used for peak shaving /grid support even though this may only occur for say 200 hours per year.
As an example if in a particular set the Standby Rating were 1000 kW, then a Prime Power rating might be 850 kW, and the Continuous Rating 800 kW. However these ratings vary according to manufacturer and should be taken from the manufacturer's data sheet.
Often a set might be given all three ratings stamped on the data plate, but sometimes it may have only a standby rating, or only a prime rating.

## Slide 13
Fuels
Diesel fuel is named after diesel engines, and not vice versa; diesel engines are simply compression-ignition engines, and can operate on a variety of different fuels, depending on configuration and location. Where a gas grid connection is available, gas is often used, as the gas grid will remain pressurized during almost all power cuts. This is implemented by introducing gas with the intake air and using a small amount of diesel fuel for ignition. Conversion to 100% diesel fuel operation can be achieved instantaneously.[14]

## Slide 14
Fuels
In more rural situations, or for low load factor plant, diesel fuel derived from crude oil is a common fuel; it is less likely to freeze than heavier oils. Endurance will be limited by tank size. Diesel engines can work with the full spectrum of crude oil distillates, from natural gas, alcohols, gasoline, wood gas to the fuel oils from diesel oil to cheaper residual fuels that are like lard at room temperature, and must be heated to enable them to flow down a fuel line.[15]

## Slide 15
Larger engines (from about 3 MWe to 30 MWe) sometimes use heavy oils, essentially tars, derived from the end of the refining process.
The slight added complexity of keeping the fuel oil heated to enable it to flow, whilst mitigating the fire risks that come from over-heating fuel, make these fuels unpopular for smaller, often unmanned, generating stations.
Other possible fuels include: biodiesel, straight vegetable oil, animal fats and tallows, glycerine, and coal-water slurry.

## Slide 16: Sample
Commercial/Industrial GenSets
Cummins Power Generation products include:
Diesel engine generator sets in the 7 kW to 2.7 MW range
Spark–ignited natural gas/propane engine generators in the 7 kW to 150 kW range
Lean–burn gas engine generators in the 315 kW to 2 MW range

## Slide 17
Diesel Generator Sets
Diesel powered generator sets remain the number–one choice for standby and emergency power systems, worldwide.
Able to start and assume load in less than 10 seconds, and rated load in a single step, Cummins diesel generator sets are the epitome of rugged dependability and reliable mechanical and electrical performance.
Diesel generators are also well suited to utility peaking plants, Distributed Generation (DG) facilities, peak shaving (or peak lopping), and power management at large commercial or industrial sites.

## Slide 18
Spark-Ignited Generator Sets – Natural Gas and Propane
Our spark–ignited generator sets, 6.0 to 150 kW, are designed for applications that call for gaseous fuel options as a result of fuel containment, economic and emissions considerations, or compliance with local codes.
These generator sets have fuel systems for both natural gas and propane, making them a convenient choice for a variety of life–support and related applications, including small health care facilities and retail businesses.

## Slide 19
Lean–Burn Gas Generator Sets
Cummins lean–burn natural gas engine generator sets are available in sizes ranging from 315kW to 2 MW.
These feature very low emissions and are suitable for prime power and combined heat and power (CHP) applications.
Low BTU fuel option on specific models.

## Slide 20: If you think standby generation may be a fit for your application, you should consider:
How much energy capacity do you need?
How many hours per year do you expect to operate?
Will you be using natural gas or diesel fuel?
How much stored on-site fuel capacity do you need?
What are the interconnect requirements to operate in parallel?
Closed or open transition?
What are the challenges associated with obtaining an environmental permit given your existing emissions profile?
Does your local utility company or regional transmission independent system operator (ISO) have an interruptible, peaking or demand response program?

## Slide 21: If you think standby generation may be a fit for your application, you should consider:
Who decides when you operate your standby generation plant and for how long?
Do you have enough space for the equipment onsite?
Will you need a transformer to match incoming utility voltage?
Does your facility have capacitor banks?
Do you need an uninterruptible power supply (UPS) for sensitive equipment and data center or information technology (IT) infrastructure?
Do you have the expertise to operate and maintain the equipment (i.e., is it part of your core business)?

## Slide 22: Thank you for coming
.